## Sheet1
3 | DDC 3 - Lower Ground - P1.2
Item No. | Device | Point's Tag | QTY | DI | DO | AI | AO | Total Points |  |  |  | Integration Connection / Route DDC / Route GW | Requirements / Field Devices
[8 empty] | DI/BI | DO/BO | AI/UI | AO/UO
1 | Lighting Control System | Integration With LCP | 1 |  |  |  |  | BACnet/IP Integration |  |  |  | IP Integ with Server Directly | #REF!
|  | Lighting Switch Start/Stop Command | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0
|  | Lighting Switch On/Off Status | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
2 | Electrical Vehicle Charging System | Integration With Electrical Vehicle Charging System | 18 |  |  |  |  | BACnet/IP Integration |  |  |  | IP Integ with Server Directly | #REF!
|  | Over-Voltage Alarm | 18 |  |  |  |  | Software Points
|  | Undervoltage Alarm | 18
|  | High Temperature Alarm | 18
|  | Low Temperature Alarm | 18
|  | Charge/Discharge Overload Alarm | 18
|  | Short Circuit Alarm | 18
3 | Auditorium | Integration With Auditorium | 1 |  |  |  |  | Physical Points
|  | General Alarms | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
4 | Access Control System | Integration With Access Control Sys. | 1 |  |  |  |  | BACnet/IP Integration |  |  |  | IP Integ with Server Directly | #REF!
|  | Panel Trip Alarm | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Panel On/Off Status | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
5 | Auditorium AV System | Integration With Auditorium AV System | 1 |  |  |  |  | BACnet/IP Integration |  |  |  | IP Integ with Server Directly | #REF!
|  | General Alarms | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
6 | Motorized Damper | QTY. of Devices | 1 |  |  |  |  | Physical Points
|  | Fire Damper Open/Close Control Signal | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | from FACP
|  | Fire Damper Open/Close Status | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Isolation Damper Diff. Pressure Feedback | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 |  | by others
7 | SMDB/ESMDB Panels | QTY. of Devices | 1 |  |  |  |  | Physical Points
| (MB-SS-SMDB) | Incoming Trip Alarm | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Incoming On/Off Status | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Incoming Power Fail | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Outgoing Trip Alarm | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Outgoing On/Off Status | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
8 | UDB/UPP panel | QTY. of Devices | 1 |  |  |  |  | Physical Points
| (MB-LG-UPP2) | Incoming Trip Alarm | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Incoming On/Off Status | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Outgoing Trip Alarm | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Outgoing On/Off Status | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
9 | Fire Fighting Panels | QTY. of Devices | 1 |  |  |  |  | Physical Points
|  | Power Supply Available | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Control Panel Alarm Status | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Manifold Release | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
10 | Submersible Pumps | QTY. of Devices | 1 |  |  |  |  | Physical Points
| 2 Sets (1 Duty & 1 Standby) | Pump Start/Stop Command | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0
|  | Pump On/Off Status | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Pump Trip Alarm | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Pump Dry Run Alarm | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Level Indicator | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 |  | By Others
11 | Fuel Transfer Pumps | QTY. of Devices | 1 |  |  |  |  | Physical Points
| 2 Acting | Pump Start/Stop Command | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 |  | From Pumps Control Panel
|  | Pump On/Off Status | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Pump Trip Alarm | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Pump Auto Status | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | Dry Run Alarm | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  | System Pressure | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
|  | Spare Physical Points | 20% |  |  |  |  | 0 | 0 | 0 | 0
|  | DDC Total Physical Points | 32 |  |  |  |  | 26 | 3 | 3 | 0
|  | DDC Total Integration Devices / Points | 21 |  |  |  |  | 0 |  |  |  | #REF!